How to setup

a remote driver

in

a redundant project

Author		:	Frenk Mulder

Document	:	/tmp/in/input.doc

Date		:	5/2/2006

Revision	:	1.0

Table of contents

1	Introduction	1

2	Redundant scenarios	2

2.1	Introduction	2

2.2	Scenario 1 : Connection can’t be shared	3

2.3	Scenario 2 : Connection can be shared	4

2.3.1	Project 1	5

2.3.2	Project 2	6

# Introduction

Setting up a remote driver in a redundant PVSS project can be done in various ways. The approach to take depends on the connected field-hardware.

A ‘remote’ driver means that the PVSS driver does not run on the same computer as the PVSS event manager. This can have various reasons.

- The PVSS server could be far away from the field-device. Placing an extra computer ( with a remote driver ) next to the device could be a solution ( example: the field device has s short serial line )

- Easier to configure. When a PVSS OPC client has to communicate with an OPC server on a different computer then normally DCOM would be necessary to establish a bridge over the network.
When you put the PVSS opc client on the remote computer ,then DCOM would not be necessary. This has several advantages:
- Easier to setup 	( DCOM is quite complex )
- Easier to monitor 	( the status of a PVSS opc client is monitored automatically )

- Performance reasons
You may decide to put communication tasks on a different computer when there is a lot of devices to be queried.

This document will describe 2 scenarios and the steps to set it up.

As an example we’ll assume that the driver that we need is a ‘PVSS opc client’

Frenk Mulder

6/2/2006

# Redundant scenarios

## Introduction

There are basically 2 scenarios when setting up a remote driver for a redundant project:

- Connection to device can’t be shared

The connection to the field-device can’t be shared. For example: the driver is going to communicate via a RS232 line. This means that one driver has to run, that provides data to both PVSS servers

The disadvantage of this approach is clear. There are several ‘single point of failure’s.

- The serial cable could go down
- The (single) driver could go down

Both PVSS servers would stop receiving data

- Connection to device can be shared. 

The field-device could be a PLC with an ethernet connection where multiple clients are allowed. Each PVSS server could have its own driver

## Scenario 1 : Connection can’t be shared

Assume that we have the following configuration

The ‘remote driver PC’ called ‘DRIVER1’ has an RS232 connection to a serial device. A serial line can’t be shared between multiple drivers and thus : one driver must be started on this computer that provides data to both servers:

To setup this driver on the computer ‘DRIVER1’

- Setup a regular PVSS project

- The config file should have entries to define the location of the event- and data manager.

event = “pvss_main$pvss_backup”
data = “pvss_main$pvss_backup”

when the network cabling is also redundant then the config file should look like:

event = “pvss_main-1, pvss_main-2$pvss_backup-1, pvss_backup-2”
data = “pvss_main-1, pvss_main-2$pvss_backup-1, pvss_backup-2”

- Add an OPC client in the PVSS console and assign it a number:

PVSS00OPC –num 2

- This opc client ( note the number 2 ) must deliver his data to both servers. This means that we have to add an entry to the config file ( \config\config ):

[opc_2]
connectToRedundantHosts = 1

Note:
The keyword ‘opc_2’ ofcourse refers to the driver number ‘-num 2’

## Scenario 2 : Connection can be shared

There are many scenarios where a connection can be shared.

- A PLC could have an ethernet connection.

- You might have a remote computer with an OPC server and you may wish to put a ‘PVSS opc client’ on this computer.

Lets assume the following configuration:

The computer ‘OPCSERVER1’ has an OPC server whose data needs to be communicated to PVSS servers ‘PVSS_MAIN” and ‘PVSS_BACKUP’

Note on scenario1:
We could ofcourse decide to put a single PVSS OPC client on this computer ‘OPCSERVER1’ and use the config entry ‘connectToRedundantHosts’ to send its data to both servers.
However, this driver then becomes a ‘single point of failure’. When the driver is stopped, then both PVSS servers no longer receive any data.

Lets also assume that we may wish to start an editor ( GEDI ) or a user interface ( NV ) on this remote computer ‘OPCSERVER1’.

There will be two OPC clients on the computer ‘OPCSERVER1’. These 2 clients will both have their own settings. This means that we’ll need 2 different PVSS projects.

We’ll need the following project ( name is arbitrary )

| Project name | Description |
| --- | --- |
| Project1 | This project will have: - an opc client that connects to PVSS_MAIN - a user interface that connects to both servers |
| Project2 | This project will have - an opc client that connects to PVSS_BACKUP We’ll have to change the config settings in this project so that the driver assumes that he is the backup driver. |

### Project 1

To setup the first project:

- Create a project called ‘PROJECT1’	( name is arbitrary ! )

- Define an entry for the OPC client. 

Example:
When the OPC client has number 2 then the config file should say:

  [general]
  pmonPort = 4999

  [opc]
  drvDpName = "_Driver2"
  server = "ABB" "ABB.AC800MC_OpcDaServer.3"
  IOTransitionTimeout = 5

- Create an opc client in the console with:

PVSS00OPC –num 2 –event “PVSS_MAIN” –data “PVSS_MAIN”

or

PVSS00OPC –num 2 –event “PVSS_MAIN-1, PVSS_MAIN-2” –data “PVSS_MAIN-1, PVSS_MAIN-2”

### Project 2

The second OPC client on the computer ‘OPCSERVER1’ must connect to the backup computer.

- Create a project called ‘PROJECT2’	( name is arbitrary ! )

- Define an entry for the OPC client. 

  [general]
  pmonPort = 4998

  [opc]
  drvDpName = "_Driver2_2"
  server = "ABB" "ABB.AC800MC_OpcDaServer.3"
  reduPostfix = "_2"
  IOTransitionTimeout = 5

- Create an opc client in the console with:

PVSS00OPC –num 2 –event “PVSS_BACKUP” –data “PVSS_BACKUP”

or

PVSS00OPC –num 2 –event “PVSS_BACKUP-1, PVSS_BACKUP-2” –data “PVSS_BACKUP-1, PVSS_BACKUP-2”